## Slide 1: Lesson 04 Creating a Human-Machine Interface for an OpenPLC Program
Dr. David J. Coe
Electrical and Computer Engineering Department
University of Alabama in Huntsville
coed@uah.edu

## Slide 2: Outline
Introduction
ScadaBR Installation
Creating an HMI Using ScadaBR
  Configuring Data Source
  Creating HMI View
Suggested Reading
Hands-On Laboratory Exercise #4

## Slide 3: Introduction

## Slide 4: Definition
Human-Machine Interface (HMI)
The interface used by the human operator to monitor and control operation of the PLC as it exercises control of some physical process

## Slide 5: ScadaBR
An open-source tool that allows one to create a custom HMI that interacts with one or more PLCs using industry standard communication protocols such as Modbus
ScadaBR requests information from the PLC via internet packets
  Contact status, coil status, etc.
PLC responds by sending the information back to ScadaBR for display

## Slide 6: Entered / Simulated Ladder Logic and Generated Structured Text
LED lights whenever PB2 is pressed
LED lights for 2 sec after PB1 is pressed

## Slide 7: Uploaded Program Compiled and Executing on OpenPLC

## Slide 8: ScadaBR Installation

## Slide 9: Follow OpenPLC Project Directions
https://www.openplcproject.com/reference-installing-scadabr

## Slide 10: Screenshot of Pre-built ScadaBR VM
https://www.openplcproject.com/reference-installing-scadabr
Check your network setup if no IP address visible here

## Slide 11: Creating an HMI Using ScadaBR

## Slide 12: HMI Creation with ScadaBR
Start your OpenPLC program running on your OpenPLC virtual or physical instance
Use your browser to access URL
  ScadaBR-IP-Here:8080/ScadaBR
Login using username admin / password admin
Configure and enable data source
Create an HMI view to show PLC program status

## Slide 13: Configuration of Data Source

## Slide 14: Configuration of Data Source - 1
From the View tab, select Modbus IP option

## Slide 15: Configuration of Data Source - 2
From the View tab, select Add option to create a new view

## Slide 16: Configuration of Data Source - 3
View configuration options

## Slide 17: Configuration of Data Source - 4
Set name, host, and update period options
Hit Save icon
For Transport type, TCP works, TCP with Keep-Alive is more reliable

## Slide 18: Configuration of Data Source - 5
Set number of registers to 10 and register range to Input status

## Slide 19: Configuration of Data Source - 6
Test ScadaBR to OpenPLC connectivity
Hit Read Data icon with and without holding push buttons (input status)
Repeat for LED (change register range to output status)
If you see state change, then ScadaBR is interacting with OpenPLC
Verify Push Button #2 input status change
Verify LED output status change

## Slide 20: Configuration of Data Source - 7
ScadaBR has been correctly configured to communicate with OpenPLC
Now we need to select specific data points to monitor via the HMI
Scroll down and hit Add point

## Slide 21: Configuration of Data Source - 8
Enter name of output coil LED
Set Register range to coil status
Scroll down and hit Save icon

## Slide 22: Configuration of Data Source - 9
MyLED point row added
Status is by default disabled
Click icon under Status to enable

## Slide 23: Configuration of Data Source - 10
Repeat Add point for Button1 and Button2
Be sure to change Register range to Input status
Click icons under Status to enable

## Slide 24: Configuration of Data Source - 11
Click enable icon next to save icon
Click Save icon

## Slide 25: Configuration of Data Source - 12
Click icon under Status to enable

## Slide 26: Creating an HMI View

## Slide 27: Create an HMI View of Data Points - 1
Hit Graphical view icon

## Slide 28: Create an HMI View of Data Points - 2
Hit New view icon

## Slide 29: Create an HMI View of Data Points - 3
Enter the name for the new view

## Slide 30: Create an HMI View of Data Points - 4
Add a binary graphic component to the new view

## Slide 31: Create an HMI View of Data Points - 5
Binary graphic component to new view
Hover to see component menu

## Slide 32: Create an HMI View of Data Points - 6
Each component has multiple options in its pull-down
You will need to make modifications at both places indicated

## Slide 33: Create an HMI View of Data Points - 7
Select point from data source
Give point shortcut name
Select Save

## Slide 34: Create an HMI View of Data Points - 8
Select light bulb for Image set
Select image shown for 0 and image shown for 1
Select Save icon

## Slide 35: Create an HMI View of Data Points - 9
Press and hold Push Button #2 on physical circuit
Bulb should light when pressed and darken upon release

## Slide 36: Create an HMI View of Data Points - 10
Add binary graphic components for Button #1 and Button #2
See above for binary image suggestion

## Slide 37: Create an HMI View of Data Points - 11
Hit Save to save work and exit view editor

## Slide 38: Create an HMI View of Data Points - 12
Press and hold Button #2
Release Button #2
Test operation of HMI view and data source

## Slide 39: Create an HMI View of Data Points - 13
Press and hold Button #1
Release Button #1
LED remains on for 2 sec
Test operation of HMI view and data source
LED now off

## Slide 40: Suggested Reading
The OpenPLC Project
  https://www.openplcproject.com/
Tommy Morris – Six SCADA Modules
  https://clark.center/details/tommy_morris/Six%20SCADA%20Modules

## Slide 41: Hands-On Laboratory Exercise #4

## Slide 42: Laboratory Exercise #4 Instructions - 1
Objectives
  Learn how to use ScadaBR to create a simple Human-Machine Interface (HMI) for the First Project Ladder Logic program
  Learn how to test your HMI’s ability to interact with an executing OpenPLC program

## Slide 43: Laboratory Exercise #4 Instructions - 2
Be sure your OpenPLC runtime is actively executing the First Project Ladder Logic as described at the URL
https://www.openplcproject.com/reference-your-first-project
Create a simple HMI for your First Project program using one Simple Point to show the status of each push button and one Simple Point to show the status of the LED coil
  You may use the same binary graphics presented earlier in this lecture
  You may also explore alternate options for the LED such as the Lava Lamp
https://www.openplcproject.com/reference-your-first-project

## Slide 44: Laboratory Exercise #4 Instructions - 3
Demonstrate HMI operation by replicating all possible push button states (as previously done with the simulator) but this time you will be using the physical circuit buttons
https://www.openplcproject.com/reference-your-first-project

## Slide 45: Laboratory Exercise #4 Instructions - 4
Sample Deliverables
  Zip file of entire project directory including structured text code
  Screenshots of HMI output for each possible combination of input states